## Hüllflächen, Himmelsricht.
Enveloping Surfaces of Zones in an Example Swimming Pool
| Zone 1 |  | Zone 2 |  | Zone 3 |  | Zone 4 |  | Zone 5 |  | Zone 6 |  | Zone 7 | Zone 8
Zone designation | Eingangsbereich |  | Umkleiden |  | Duschen und Sanitärräume |  | Schwimmhalle |  | Aufsichtsraum |  | Saunabereich |  | Fitness | Technikraum
Outer walls and cardinal directions of them, including transparent elements [m²] | N | 24 | N | 0 | N | 105 | N | 70 | N | 0 | N |  | N | N | 0
| E | 100 | E | 0 | E | 0 | E | 20 | E | 0 | E |  | E | E | 0
| S | 24 | S | 0 | S | 0 | S | 85 | S | 0 | S |  | S | S | 0
| W | 15 | W | 22.5 | W | 22.5 | W | 100 | W | 0 | W |  | W | W | 0
Transparent elements in outer walls in each cardinal direction [m²] | N | 0 | N | 0 | N | 0 | N | 0 | N | 0 | N |  | N | N | 0
| E | 40 | E | 0 | E | 0 | E | 0 | E | 0 | E |  | E | E | 0
| S | 0 | S | 0 | S | 0 | S | 90 | S | 0 | S |  | S | S | 0
| W | 0 | W | 0 | W | 0 | W | 0 | W | 0 | W |  | W | W | 0
Roof (upper building closure, including horizontal transparent elements) [m²] |  | 210 |  | 262.5 |  | 262.5 |  | 700 |  | 20 |  |  |  |  | 700 | Zone 2 identical to zone 3?
Transparent horizontal elements [m²] |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | 0
Ground floor (lower building closure) including pool floor with earth contact [m²] |  | 210 |  | 262.5 |  | 262.5 |  | 700 |  | 20 |  |  |  |  | 700
Inner walls and inner ceilings as a sum [m²] |  | 125 |  | 22.5 |  | 256.5 |  | 170 |  | 39 |  |  |  |  | 0
Total area of zone (including water surface) [m²] |  | 163.9 |  | 202.3 |  | 70.7 |  | 900 |  | 20 |  |  |  |  | 700 | From Schwimmbad Calculator, does not fit to wall values
Traffic and common area above technical room [m²] | [7 empty] | 194
Air volume [m³] |  | 491.7 |  | 618.9 |  | 212.2 |  | 3600 |  | 50 |  |  |  |  | 2353
Total pool floor [m²] | [7 empty] | 569.5
Water areas of pools [m²] | [6 empty] | SB | 312.5 | [7 empty] | SB=Schwimmerbecken, MZB=Mehrzeckbecken, NSB=Nichtschwimmerbecken, SPB=Springerbecken, KB=Kleinkinderbecken, VB=Variobecken, FB=Freiformbecken
[7 empty] | MZB | 120
[7 empty] | KB | 15
[7 empty] | NSB | 36
[7 empty] | SPB | 36
[7 empty] | FB | 50
Pool floor with earth contact [m²] | [6 empty] | SB | 62.5
[7 empty] | MZB | 0
[7 empty] | KB | 0
[7 empty] | NSB | 0
[7 empty] | SPB | 36
[7 empty] | FB | 0
Water temperature [°C] | [6 empty] | SB | 26
[7 empty] | MZB | 26
[7 empty] | KB | 28
[7 empty] | NSB | 26
[7 empty] | SPB | 26
[7 empty] | FB | 26
Water volume [m³] | [6 empty] | SB | 937.5
[7 empty] | MZB | 162
[7 empty] | KB | 9
[7 empty] | NSB | 48.6
[7 empty] | SPB | 122.4
[7 empty] | FB | 67.5
Plausibility Check of Zone Parameters with reference building volume (aspect ratio: 2 by 1)
Roof area= ground floor area (including floor of pools with ground contact) | TRUE
comparing sum of outer walls with reference building volumes walls (between 80% and 120% of refernce value) | größer 80% | TRUE | Kleiner 120% | TRUE
reference building calculated with total zones volume, ground floor and sides ratio of 2:1 | total volume [m³] | 7325.8 | ground floor [m²] | 2155 | reference side A [m] | 32.8 | reference side b = 2x side A [m] | 65.6 | reference height [m] | 3.4 | reference sum of outer wall [m²] | 669.12

## Zonenbeschreibung
Zone | enthaltene Räume/Bereiche
1a | Foyer/Kasse
1a | Verwaltung / Personal
1a | Lagerräume (Müll, etc.)
1a | ergänzende Verkehrsfläche zu Zone 1
1b | Funktionsraum Chlor
1c | Gastro extern
2 | Umkleide
2 | erg. Verkehrsfläche Zone 2
3a | Duschen/WC Badebereich
3a | erg. Verkehrsfläche Zone 3a
3b | Duschen/WC Saunabereich
4a | Badebereiche
4a | Rutschenturm, Rutsche
4a | Nebenräume Badeebene/ Lager
4a | erg. Verkehrsflächen Zone 4a
4b | Gastro intern
5 | Aufsicht / 1. Hilfe
6 | Saunabereich
6 | Massage
6 | Wellness
7 | Fitness
8 | Technik (HLSB + E)

## Strukturen Hüllfläche-Bürodaten
Building Envelope Structures in Swimming Pools
name | building age start | building age end | heat transmission coefficient (U) | g-value | layer | thickness | thickness | thermal conductivity | material (from document "zone interaction 26.06.") | material (proposed) | material (German) | material id | inner radiation | inner convection | outer radiation | outer convection
| [a] | [a] | [W/(m²K)] |  | (from inside 0 to outside X) | [m] | [cm] | [W/mK]
OuterWall_A | 0 | 2000 | 0,211 (highest value in BMVBS_2011_Typologie is 0,35) |  | 0 |  | 1 |  | tiles | tiles |  |  | 5.0 | 2.7 | 5.0 | 20.0 | Maybe: brick_intern_DK with thermal conduct. of 0,68 | missing allocation to zones and components described there, please validate and complete parameters
[5 empty] | 1 |  |  |  | vapour_barrier | vapour_barrier
[5 empty] | 2 |  | 20 |  | concrete | concrete_wz05 | Beton_wz05 | 249f131a-3a43-11e7-b4e6-2cd444b2e704 |  |  |  |  | Alternative: Beton_CEM_II_BS325R_wz05
[5 empty] | 3 |  | 20 |  | thermal_insulation | mineral_wool_040 | Mineralwolle_040 | 35d01e70-3a43-11e7-a6cf-2cd444b2e704 |  |  |  |  | Alternative: insulation 036/039/042/045/060
[5 empty] | 4 |  | 3 |  | finishing | lime_plaster | Kalkputz | 2e2c8180-3a43-11e7-a6be-2cd444b2e704
OuterWall_B | 2000 | 2015 | 0,3 (highest value in BMVBS_2011_Typologie is 0,35) |  | 0 |  | 1 |  | tiles | tiles |  |  | 5.0 | 2.7 | 5.0 | 20.0
[5 empty] | 1 |  |  |  | vapor_barrier | vapor_barrier
[5 empty] | 2 |  | 20 |  | concrete | concrete_wz05 | Beton_wz05 | 249f131a-3a43-11e7-b4e6-2cd444b2e704 |  |  |  |  | Alternative: Beton_CEM_II_BS325R_wz05
[5 empty] | 3 |  | 20 |  | thermal_insulation | mineral_wool_040 | Mineralwolle_040 | 35d01e70-3a43-11e7-a6cf-2cd444b2e704 |  |  |  |  | Alternative: insulation 036/039/042/045/060
[5 empty] | 4 |  | 5 |  | air | air_layer | Luftschicht | b362502c-3f99-11e7-b117-2cd444b2e704
[5 empty] | 5 |  |  |  | facade_panels
OuterWall_C | [12 empty] | 5.0 | 2.7 | 5.0 | 20.0
OuterWall_D | [12 empty] | 5.0 | 2.7 | 5.0 | 20.0
InnerWall_A_aerated_concrete |  |  | 0.25 | [9 empty] | 5.0 | 2.7 | 5.0 | 20.0
InnerWall_B_drywall | 0 | 2015 | 0.6 |  | 0 |  | 1.25 |  | Ausbauplatte | plasterboard | Gipskartonplatte | 27068cc0-3a43-11e7-bc9e-2cd444b2e704 | 5.0 | 2.7 | 5.0 | 20.0
[5 empty] | 1 |  | 1.25 |  | Ausbauplatte | plasterboard | Gipskartonplatte | 27068cc0-3a43-11e7-bc9e-2cd444b2e704
[5 empty] | 2 |  | 10 |  | thermal_insulation | mineral_wool_040 | Mineralwolle_040 | 35d01e70-3a43-11e7-a6cf-2cd444b2e704 |  |  |  |  | Alternative: insulation 036/039/042/045/060
[5 empty] | 3 |  | 1.25 |  | Ausbauplatte | plasterboard | Gipskartonplatte | 27068cc0-3a43-11e7-bc9e-2cd444b2e704
[5 empty] | 4 |  | 1.25 |  | Ausbauplatte | plasterboard | Gipskartonplatte | 27068cc0-3a43-11e7-bc9e-2cd444b2e704
Window_A_facade_triple_glazing |  |  | 0.9 | [9 empty] | 5.0 | 2.7 | 5.0 | 20.0
Window_B_interior_double_glazing |  |  | 1.5 | [9 empty] | 5.0 | 2.7 | 5.0 | 20.0
Window_C | [12 empty] | 5.0 | 2.7 | 5.0 | 20.0
Ceiling_A_roof |  |  | 0.19 | [9 empty] | 5.0 | 2.7 | 5.0 | 20.0
Ceiling_B_heated_space_above |  |  | 0.3 | [9 empty] | 5.0 | 2.7 | 5.0 | 20.0
Rooftop_Test | 0 | 2015 |  |  | 0 |  | 15 |  | finishing | finishing |  | 253f8030-3a43-11e7-8735-2cd444b2e704 | 5.0 | 2.7 | 5.0 | 20.0
[5 empty] | 1 |  | 7 |  | thermal_insulation | mineral_wool_040 | Mineralwolle_040 | 48037df6-3a43-11e7-bd90-2cd444b2e704 |  |  |  |  | Alternative: insulation 036/039/042/045/060
[5 empty] | 2 |  | 3 |  | reinforced_concrete | reinforced_concrete |  | 2f36c3b6-3a43-11e7-9a7e-2cd444b2e704
Floor_Test | 0 | 2015 |  |  | 0 |  | 4 |  | finishing | finishing |  | 6755e6e6-3a43-11e7-adad-2cd444b2e704 | 5.0 | 2.7 | 5.0 | 20.0
[5 empty] | 1 |  | 3 |  | thermal_insulation | mineral_wool_040 | Mineralwolle_040 | 25d281da-3a43-11e7-8191-2cd444b2e704 |  |  |  |  | Alternative: insulation 036/039/042/045/060
[5 empty] | 2 |  | 15 |  | reinforced_concrete | reinforced_concrete |  | 253f8030-3a43-11e7-8735-2cd444b2e704
Ceiling_Test | 0 | 2015 |  |  | 0 |  | 15 |  | finishing | finishing |  | 253f8030-3a43-11e7-8735-2cd444b2e704 | 5.0 | 2.7 | 5.0 | 20.0
[5 empty] | 1 |  | 3 |  | thermal_insulation | mineral_wool_040 | Mineralwolle_040 | 25d281da-3a43-11e7-8191-2cd444b2e704 |  |  |  |  | Alternative: insulation 036/039/042/045/060
[5 empty] | 2 |  | 4 |  | reinforced_concrete | reinforced_concrete |  | 6755e6e6-3a43-11e7-adad-2cd444b2e704
Floor_A_above_non_heated | 0 | 2015 | 0.231 |  | 0 |  |  |  | finishing | finishing |  |  | 5.0 | 2.7 | 5.0 | 20.0
[5 empty] | 1 |  |  |  | PE_foil | polyethylene_foil_2 | Polyethylene_Folie_2 | 39c59c0c-3a43-11e7-ac33-2cd444b2e704
[5 empty] | 2 |  | 20 |  | thermal_insulation | mineral_wool_040 | Mineralwolle_040 | 35d01e70-3a43-11e7-a6cf-2cd444b2e704 |  |  |  |  | Alternative: insulation 036/039/042/045/060
[5 empty] | 3 |  | 4 |  | leveling_zementestrich | cement_floating_screed_2_bottom | Schwimmender_Estrich | 6755e6e6-3a43-11e7-adad-2cd444b2e704
[5 empty] | 4 |  | 15 |  | reinforced_concrete | reinforced_concrete
[5 empty] | 5 |  |  |  | waterproofing | waterproofing
[5 empty] | 6 |  | 10 |  | concrete | concrete_wz05 | Beton_wz05 | 249f131a-3a43-11e7-b4e6-2cd444b2e704 |  |  |  |  | Alternative: Beton_CEM_II_BS325R_wz05
[5 empty] | 7 |  |  |  | gravel | gravel_mixed_granular | Kies_gemischt_körnig | 2f52f9ee-3a43-11e7-ae5e-2cd444b2e704 |  |  |  |  | Alternative: gravel_single_granular
Floor_B_above_heated_4-8 |  |  | 0.281 |  | 0 |  |  |  | finishing | finishing |  |  | 5.0 | 2.7 | 5.0 | 20.0
[5 empty] | 1 |  | 12 |  | thermal_insulation | mineral_wool_040 | Mineralwolle_040 | 35d01e70-3a43-11e7-a6cf-2cd444b2e704 |  |  |  |  | Alternative: insulation 036/039/042/045/060
[5 empty] | 2 |  | 40 |  | reinforced_concrete | reinforced_concrete
[5 empty] | 3 |  |  |  | finishing | finishing
GroundFloor_Test | 0 | 2015 | 0.281 |  | 0 |  | 4 |  |  | cement_floating_screed_2_bottom |  | 6755e6e6-3a43-11e7-adad-2cd444b2e704 | 5.0 | 2.7 | 5.0 | 20.0
[5 empty] | 1 |  | 3 |  |  | EPS_040_15 |  | 25d281da-3a43-11e7-8191-2cd444b2e704 |  |  |  |  | Alternative: insulation 036/039/042/045/060
[5 empty] | 2 |  | 15 |  |  | concrete_CEM_II_BS325R_wz05 |  | 253f8030-3a43-11e7-8735-2cd444b2e704

## Vorschläge DGfdB
|  |  | Layer 1 |  |  | Layer 2 |  |  | Layer 3 |  |  | Layer 4 |  |  | Layer 5 |  |  | Layer 6 |  |  | Layer 7 |  |  | Layer 7 |  |  | U value
|  | Inside | Material | Thickness | λ | Material | Thickness | λ | Material | Thickness | λ | Material | Thickness | λ | Material | Thickness | λ | Material | Thickness | λ | Material | Thickness | λ | Material | Thickness | λ
|  |  |  | mm | W/mK |  | mm | W/mK |  | mm | W/mK |  | mm | W/mK |  | mm | W/mK |  | mm | W/mK |  | mm | W/mK |  | mm | W/mK
Wall_A | Facade wall |  | Tiles | 10 |  | Vapor barriere |  |  | Concrete | 200 |  | Thermal insulation | 200 |  |  |  |  | Finishing | 30 | [7 empty] | 0.211 | W/m2K
(optional)
Wall_B | Facade wall |  | Tiles | 10 |  | Vapor barriere |  |  | Concrete | 200 |  | Thermal insulation | 200 |  | Air | 50 |  | Facade panels | [8 empty] | 0.3 | W/m2K
(optional)
Wall_C | [27 empty] | W/m2K
Wall_D | [27 empty] | W/m2K
Wall_E | Porenbeton | [25 empty] | 0.25 | W/m2K
Wall_F | Drywall |  | Ausbauplatte | 12.5 |  | Ausbauplatte | 12.5 |  | Insulation | 100 |  | Ausbauplatte | 12.5 |  | Ausbauplatte | 12.5 | [10 empty] | 0.6 | W/m2K
Glass_A | Facade, triple glass | [25 empty] | 0.9 | W/m2K
Glass_B | Interior, double glass | [25 empty] | 1.5 | W/m2K
Glass_C | [27 empty] | W/m2K
Ceiling_A | roof | [25 empty] | 0.19 | W/m2K
Ceiling_B | heated space above | [25 empty] | 0.3 | W/m2K
Floor_A | above non heated |  | Finishing |  |  | PE foil |  |  | Thermal Insulation | 200 |  | Leveling zementestrich | 40 |  | Reinforced concrete | 150 |  | Waterproofing |  |  | Concrete | 100 |  | Gravel |  |  | 0.231 | W/m2K
Floor_B | Above heated 4-8 |  | Finishing |  |  | Thermal Insulation | 120 |  | Reinforced concrete | 400 |  | Finishing | [14 empty] | 0.281 | W/m2K